Preliminary stages of a PV project

   Concise guide for:

- projects of more than 100 solar panels

- public-sector organisations and private organisations

- How to ensure good prices and good quality

- Safety and fire safety

- Sustainability options

- Practical tips with the names

of technical advice consultancy firms

Preliminary stages of a PV project

   Concise guide for:

- projects of more than 100 solar panels

- public-sector organisations and private organisations

- How to ensure good prices and good quality

- Safety and fire safety

- Sustainability options

- Practical tips with the names

of technical advice consultancy firms

public-buyers-community.ec.europa.eu

public-buyers-community.ec.europa.eu

An initiative from: RVO and PIANOo

Version: 0.99 (Draft)

Authored by Michiel Mensink and Marcello Passaro, 
with copyright attributed to Rijksdienst voor Ondernemend Nederland, 2023.

Date of publication: 5 September 2023

An initiative from: RVO and PIANOo

Version: 0.99 (Draft)

Authored by Michiel Mensink and Marcello Passaro, 
with copyright attributed to Rijksdienst voor Ondernemend Nederland, 2023.

Date of publication: 5 September 2023

Table of contents

Table of contents	1

Objective of and background  to this guide	3

Why	3

Edits requested!  Please send us an email to” bigbuyers@eurocities.eu	3

Responsibility	4

Disclaimer	4

Introduction	5

The Preliminary Study	6

Step 1 Stock-taking	7

1.1 General	7

1.2 Electrical considerations	7

1.3 Photos and maps	7

1.4 Planning	7

1.5 Roof load	7

Step 2. Indicative engineering	8

2.1 Determining the maximum number of solar panels and maximum generation of power	8

2.2 Draw up the broad outlines of the business case	8

2.3 Determining indicative power generation, project costs and the number of solar panels	9

2.4 Optional	9

Step 3 Ownership and issuing a call  for tenders/procurement	9

3.1 Owner or renter?	9

3.2 For public organisations: public procurement or direct award?	9

Step 4 Permits and grid connection	12

4.1 Permits	12

4.2 Connection to the grid: options and considerations	12

Step 5 Turnover, subsidies, financing and insurance	14

5.1 Turnover from the reverse supply of power	14

5.1 Subsidies	15

5.2 Financing	15

5.3 Insurance	17

Step 6 Sustainability aspects	18

6.1 Sustainability aspects of solar panels	19

6.2 Environmental aspects involved in Sun-on-Land and  Sun-on-Water	20

Step 7 Execution and delivery	21

7.1 Timelines	21

7.2 Inspections and final inspection	21

Step 8 Maintenance, Monitoring and End-of-Life	23

Abbreviations and acronyms	24

Annex 1 - Technical Consultants	25

Annex 2 - Building physics consultants, structural engineers specialising in roof load	26

Annex 3 – Installation companies,  EPCs and project developers  for PV companies	27

Annex 4 - Consultants and providers specialised in energy management systems, batteries, and demand management	29

Annex 5 - Loan capital	30

and equity capital backers	30

Annex 6 - Scope 12 inspections	31

Annex 7 - Factory audits  and sample testing	32

Annex 8 - Monitoring, maintenance  and repairs	33

Annex 9 - Overview of CAR insurance coverage	34

Section I: The works	34

Objective of and background 
to this guide

Many organisations want to implement PV projects on roofs or land. This guide will take you through the preparatory stages, setting out steps and choices, and providing lists of consultants that can assist you.

This guide is one of three documents that complement 
the ‘Template for purchase requirements and award criteria’

I. Preparatory stages of a PV project (this guide)

II. Preparing a tender for a PV project, and explanation of the Template

III. Sustainability aspects and market scan of the more sustainable solar panels

A draft of the ‘Template for purchase requirements and award criteria’ is also available. It is created as a spreadsheet that can be attached as in tender/RFQ documentatioon, after adjusting a number of project specific fields.

Objective of this guide

The objective of this guide is to help users carry out PV projects offering:

- better financial conditions

- a longer working life

- better sustainability

Why

PV projects are all too often poor value for money. Further, sustainability aspects of solar panels themselves are often not taken into consideration – think of the use of PFAS and other harmful materials, the technical working life, the carbon footprint, environmental issues and working conditions.

Edits requested!  Please send us an email to” bigbuyers@eurocities.eu

This guide is a draft version/ . It was created in the Netherlands and thereafter auto-translated without checks from native speaking PV experts. Therefore improper words will be used. Further, in your country the regulations, permits and subsidies will be different from those in the Netherlands, which were auto-translated. So the guide certainly does contain mistakes and needs to be improved. In addition, the lists in the Annexes with names of consultants/experts need to be completely modified as these are mostly Dutch organisations. It would be great if you can help us with lists consultants/experts from your country. The solar trade association in your country may help you here.

Responsibility

This guide was drawn up on the initiative of the Dutch Public Buyers Group for Sustainable PV. This Buyers’ Group consists of the Dutch Public Procurement Expertise Centre, PIANOo, and is made possible by the Ministry of Infrastructure and Water Management. . The Buyers’ Group is headed by Bart-Jeroen Bierens and Michiel Mensink from the Netherlands Enterprise Agency .

Disclaimer

The purpose of this guide is to provide assistance and support to private organisations and contracting authorities when preparing calls for tenders for PV projects. The guide was drawn up using recent insights from the sector. It may be necessary for individual calls for tenders to include criteria that are not in the guide or to adjust criteria, for example due to specific circumstances or preconditions. Both the guide and the criteria are used under the contracting authorities’ own responsibility. Users cannot make any claim based on the accuracy and completeness of the content or derive any rights therefrom.

Authors Michiel Mensink and Marcello Passaro

Copyright Rijksdienst voor Ondernemend Nederland, 2023

Introduction

PV projects usually go through the following phases:

This guide focuses on Phase I: the Preliminary study.

You need to make the main choices during the preliminary study, after which a call for tenders or RFQ (‘request for quote’) can be efficiently drafted. You can adapt the Template of requirements and award criteria to your project and add it as an annex to the RFQ or call for tenders.

The guide will address the following topics:

- Feasibility study – project size, roof load, connections to the grid

- Project size and tender limits (for public entities)

- Opting for ownership or rental of square metres?

- Financing

- Choices for the operational phase – maintenance and monitoring

- Project duration and End of Life

- Quality control

In the next version of the guide, we hope to include also:

- Energy management systems

- Storage (batteries)

- Charging points (if combined with a PV project)

The Preliminary Study

In this phase, you determine the broad outline of the project and what its needs and requirements are.

Tip 1: Call in a technical consultant!

See Annex 1 for a list of technical consultants that can help you with the preliminary stages. This is, of course, unnecessary if you have sufficient experience and knowledge or your organisation does.

Please note: the list is not exhaustive, there are many consultants who have not yet been included!

You can look at the preliminary study as a step-by-step plan:

I. Preliminary study

| 1. Stock-taking | - List of sites - Measurements per roof/plot - Photos and maintenance schedule - Roof load, grid connection and use |
| --- | --- |
| 2. Indicative engineering | - Number of panels and capacity per site - Draft business case - Indicative specifications |
| 3. Ownership and selection process | - Concession / leasing? - Direct award? - National or European call for tenders? |
| 4. Permits and grid connection | - Are environmental permits required? - Increase the grid connection? - Charging points? EMS [Energy Management System] or batteries? |
| 5. Turnover, subsidies, financing and insurances | - Sale of electricity; SDE++ [Sustainable Energy Production and Climate Transition Incentive Scheme] or other subsidies? - Financing (internal + external)? - Insurance |
| 6. Sustainability aspects | - Sustainability aspects of solar panels - Environmental issues - Working conditions |
| 7. Execution and delivery | - SCIOS Scope 12 - Other tests and inspection |
| 8. Maintenance and monitoring | - Maintenance - Monitoring |

Step 1 Stock-taking

The first step of the project is to take stock of the available roofs or plots included in the project. You can do this (in part) yourself or with the help of a technical consultant (see Tip 1). When dealing with multiple sites, an overview is often presented in a table, along with photos and maps for each site.

1.1 General

- Site address

- Short description of the site

- Rough measurements of the PV area (length x width)

- Possible start date for installation, and end date, if applicable

1.2 Electrical considerations

Take stock with the site manager/building manager:

- Any self-consumption? Is there a connection to the grid at this site?

- Size of the grid connection at this site (for example 3 x 80 A)

- Self-consumption of electricity on site

- Expected changes in electricity consumption

- Possibly: need for charging points

1.3 Photos and maps

Prepare a digital file containing site maps, satellite pictures and close-up pictures including

any obstacles.

1.4 Planning

Take stock with the site manager/building manager:

- Large-scale maintenance - for instance replacing the roof

- Plans concerning plots/roofs - is any construction/development planned in the future?

1.5 Roof load

The permitted roof load is an important parameter for ‘Zon-op-Dak’ [Sun-on-Roof] projects. In the Netherlands, around half of all roofs are not suited to a standard PV system as the ballast that prevents the panels from blowing off the roof is too heavy.

There are various solutions if the roof is too flimsy, including:

- a PV system that does not use ballast by anchoring it to the roof

- flexible solar panels that are glued onto the roof

- special lightweight solar panels (for example Solarge) or special fastening systems

- Strengthening the roof construction

The permitted roof load can be explained or calculated by the contractor or the architect of the building/roof; it may otherwise be determined by an independent building physics consultant or a structural engineer.

Tip 2: See Annex 2 for a list of independent experts that can help you with this.

Step 2. Indicative engineering

If your organisation has a lot of experience with PV projects and suitable software, you can do this yourself, otherwise you should call in a technical consultant.

This is where you determine the indicative specifications of the PV installation; this is important to ensure a clearer assignment, which, in turn, allows the contracting parties to submit a more precise offer in a shorter time frame.

2.1 Determining the maximum number of solar panels and maximum generation of power

- Determine the orientation, East-West or South, or another orientation 
            of the solar    panels

- Indicative subscription of solar panels per site

- Determine the maximum number of panels

- Determine the maximum power per site

- Determine the maximum annual generation of power

- Check whether the maximum generation of power is adapted to the existing connection

2.2 Draw up the broad outlines of the business case

- Indicative investment for installation of the PV system: per Wp and total amount in thousands of euros.

- Grid connection: adapt or not?

  - If adapting: indicative timeline from the grid operator

- Yield: SDE++ scheme or another subsidy?

  - If SDE++: check how much AC capacity you can connect at most;  
this is usually 50% at most, sometimes 70% of the DC capacity

- Yield: Forecast reduction in the quantity of electricity to be purchased and cost           savings

- Yield: Projection of income from sale of solar power

  - Possibly: How to deal with negative prices - energy management system?

2.3 Determining indicative power generation, project costs and the number of solar panels

Often, there will be a need for a number of iterations before establishing the indicative specifications, in part because it depends on various targets and limitations. The indicative specifications are:

- The total capacity of the solar panels (DC capacity)

- The AC capacity of the inverters

- The annual power generation

- The indicative project costs (DC capacity in Wp x EUR 1 per Watt)

2.4 Optional

- Phasing of sites

- Possibly: opting for monofacial/bifacial solar panels

- Possibly: for ‘Sun-on-Land’/‘Sun-on-Water’: a sun-tracking system?

Step 3 Ownership and issuing a call 
for tenders/procurement

The two previous steps broadly set out the project size and project set-up. Now it is important to look at whether you yourself want to be the owner of the PV installation or whether you rent out the roof surface or plot of land in a concession agreement. The question is then how to select a supplier or a contracting party.

3.1 Owner or renter?

If renting out, you will receive a certain price per square metre per year. Advantage: it saves you a lot of time.

Potential drawbacks are that you do not benefit as much from the financial benefits of a PV installation, that you have little say on the installation and that you give up flexibility. So, if you later want to do something else with the roof or plot, you may find yourself bound by a contract with a renter/lessee.

3.2 For public organisations: public procurement or direct award?

This point does not apply to companies or other private organisations. Private organisations can simply ask for offers from a number of potential contracting parties.

In any event, a programme of requirements is also necessary when requesting standard offers. The ‘Template for purchase requirements’ is also perfectly suited to that purpose.

The Public Procurement Act 2012 [Aanbestedingswet 2012] applies to public procurement by (semi-) public institutions in the Netherlands. The larger the project, the fewer options of possible procedures. Certain procedures (such as direct awarding) are not allowed above a certain threshold.

The thresholds depend on the type of project: ‘Works’ or a ‘Supply/Service’.

The type depends on the focus of the project:

- Supply

- Only supply of solar panels

- Only installation of the electric system and components on the DC side

- Only installation of the electric system and components on the AC side

- Works

  - The contracting party is fully responsible for implementing the project

  - Combination of design, supply and works: -> works

Furthermore, other, specific threshold amounts apply to some organisations.

The paragraph below should therefore only be taken indicatively.

Please note: These amounts apply to 2023. In 2024, the amounts will probably be

a little higher.

- Simple direct awarding

  - For Supplies: 	<  EUR 50 000

  - For Works: 	< EUR 150 000

Small-scale projects can be awarded directly to a single party, for instance your usual installation company or any other local supplier.

Advantages: Short turnaround time, low procedural costs, negotiation possible, flexibility
Disadvantages:	 Possibly not the best price/quality ratio, risk of conflict of interests.

- Multiple direct procedure

  - For Supplies to decentralised (semi) public institutions: <  EUR 215 000

  - For Supplies to organisations in, among other things, the water, energy, or transport sectors: <  EUR 431 000

  - For Works: < EUR 1 500 000

Ask for an offer from multiple suppliers. Award to the ‘Most economically advantageous tender’.

Advantages: Short turnaround time, low procedural costs, negotiation possible, flexibility

Disadvantages: Many tenderers do not see the call; there is no negotiation possible.

- National procedure: with or without a selection round

- For Supplies to decentralised (semi) authorities: <  EUR 215 000

- For Supplies to organisations in, among other things, the water, energy, or transport sectors: <  EUR 431 000

- For Works: < EUR 5 382 000

Tender notice on TenderNed and possibly in trade journals or newspapers. When using a selection round, often five suppliers are then invited to submit an offer.  
Advantages: Plenty of competition, price/quality ratio in line with the market; objective; transparent
Disadvantages: Long turnaround time, substantial procedural costs, little flexibility.

- European call for tenders: with or without a selection round.

Notice on TenderNed. When a selection round is used, often five suppliers are invited to submit an offer.

Advantages: The entire market can submit a tender; high competitive pressure; objective; transparent

Disadvantages: Long procedure; high procedural costs in the event of (too) many submissions; no negotiation possible, little flexibility

For more information on national threshold amounts: https://www.pianoo.nl/nl/inkoopproces/aanbestedingsprocedures/nationale-procedures/circulaire-grensbedragen-rijksoverheid

For more information on European threshold amounts:  
https://www.pianoo.nl/nl/regelgeving/drempelbedragen-europees-aanbesteden

Tip 3 For larger projects, > 2 MWp, Annex 3 provides a list of installation companies, project developers and EPC [Energieprestatiecontracten - Energy performance contracts] companies with experience of larger projects in the Netherlands.

Step 4 Permits and grid connection

This step will focus on environmental and building permits and also look at some options concerning connection to the grid.

4.1 Permits

Many projects are delayed because environmental permits are not applied for (in time).  
That is why it is best to apply for the necessary permits as early as possible in the process.

This can lead to additional requirements:

- For Sun-on-Roof projects, environmental permits are usually not required.  
However, a permit is required for listed buildings.

- For Sun-on-Land projects, the following permits and surveys may be required:

  - Zoning plan

  - Building permit

  - Environmental permit

  - Environmental issues/rare animal species survey

  - Archaeological survey

  - Survey into abandoned explosives

- For Sun-on-Water projects, various permits are required:

  - Environmental permit

  - Zoning plan

  - Building permit

Please note for Sun-on-Water: PV projects are not allowed for a number of types of water areas, because of vulnerable or rare species. Such areas include ponds, swamps, springs and moorland pools.

It is therefore essential to first consult the Water Authority. The Water Authority will often set project-specific requirements to a Sun-on-Water project. Furthermore, you should also take into account that Sun-on-Water is still a relatively new development. There are many different systems and materials but not yet sound standards or standardised tests for the floaters and installation systems. Even on inland waters, there is a risk that the systems will not last longer than 10 or 15 years as a result of wind and waves.

4.2 Connection to the grid: options and considerations

The options for connecting to the grid depend on the number of solar panels you choose. Sometimes, a good option is to install fewer panels than the maximum number that could be installed in order to remain within the existing grid connection.

The following questions and considerations are important to make the right choice:

- Self-consumption at the site
What is the ratio of the maximum capacity during daylight hours to consumption at the site during daylight hours and during winter and summer?

- Adapting the grid connection or installing an EMS 
The AC capacity of the inverters is usually 50-75% of the DC capacity of the solar panels. If the AC capacity is greater than the grid connection, there are two options:

Option 1 - Increase the grid connection capacity  
You should check with the grid operator what the waiting time would be and enquire about what it would cost...

- waiting times for a larger-scale grid connection can be up to five years (!)

- in addition, both up-front and annual costs can be high, making the business    case less appealing compared to remaining within the capacity of the existing connection.
   
Option 2 - Use an Energy Management System (EMS) 
An EMS continuously monitors the PV power generation and electricity consumption and ensures that the grid is never fed back more than a certain amount of power.

- Charging points and electric cars
Are there charging points for electric cars on the site or plans to have them in the short term? What does this mean in terms of the electrical connection? Is ‘smart’ charging desirable on the basis of available solar power, the power tariff or the grid connection?

- Demand management
Is it possible to run certain devices and machines in a ‘smart’ way and switch them on only at certain set times? Benefits:

  - Remaining within the existing grid connection for both consumption and generation

  - Benefiting from low prices and disconnecting when prices are high.

- Batteries
Adding batteries to an EMS provides more possibilities. In order to remain within the existing grid connection, any power generated beyond the maximum grid connection capacity can be stored in the battery.

Batteries’ payback time is currently quite long and unpredictable. The business case of different targets can be analysed: 1) cap the PV generation to within the existing connection; 2) cap the percentage of self-consumption of solar power; 3) financial optimisation.

Tip 4 Specialised consultants can also provide assistance here. You will find a (still incomplete) list of specialised consultants in Annex 4.

If it is opportune to add charging points, batteries or an EMS to the project, then the question follows of whether or not to combine this with the PV installation in a single contract/call for tenders. Preparing a separate contract or call for tenders for this may possibly reduce the degree of complexity for the client and the contracting party.

Step 5 Turnover, subsidies, financing and insurance

The previous steps determined the technical specifications. This step will look at whether or not the project is eligible for subsidies, and at financing and insurances.

5.1 Turnover from the reverse supply of power

During sunny periods, most PV installations generate considerably more power than the 
self-consumption.

The surplus power can then be fed back to the grid. What price can you achieve for this reverse supply of power? It used to be possible to conclude a contract with both a fixed price and a long duration. This allowed for a high level of certainty, but unfortunately this is no longer 
an option.

The three main options at the moment are:

- Through a contract with an electricity supplier (on an annual basis) 
You can ask several electricity suppliers for a standard fixed contract for both consumption and reverse supply. The duration is usually one year. It is uncertain how payment for reverse supply will evolve over the coming years. Indicative reverse supply price for summer 2023, for larger PV installations (>100 kWp): 3-5 cents/kWh

- Through a ‘dynamic’ contract with an electricity supplier 
A number of electricity suppliers offer a ‘dynamic’ contract, where the price per kWh varies from hour to hour. The basis of the hourly price is the EPEX day-ahead price and a surcharge.  

Please note: sometimes these prices are negative, and you will have to pay if you reverse-supply power.  
From January to the end of July 2023, this already applied to 212 hours - often around noon. In order to avoid paying for reverse supplied power, a box can be fitted that switches off the inverters during negative price hours. During those hours that have a positive energy price, you will usually receive a considerably higher price than the above-mentioned fixed reverse-supply remuneration.

- Automated trading on the EPEX day-ahead and the imbalance market 
It is also possible to conclude a contract with a trading platform. The companies trade (usually in an automated way) by means of their own software on both the EPEX day-ahead market and the intra-day/imbalance market. To that end, they fit a box that can switch the inverters on or off; this solution is available to projects above a certain size.

For all options, it can be useful to distribute the PV system over two grid connections: the main connection and a second connection (the ‘MLOEA’ - (Meerdere Leveranciers Op Één Aansluiting [Multiple Suppliers at a Single Connection] option). All own consumption comes from the main connection, while the surplus goes to the second connection. By concluding two different contracts (with different energy companies), you can achieve a higher price.

5.1 Subsidies

The main subsidy schemes are:

- Net metering scheme
The Net metering scheme (‘Salderingsregeling’) applies not only to private individuals but also to many companies, sports clubs, office, etc. The prerequisite is to have a ‘small consumption connection’, i.e. a grid connection with a capacity of less than 3 x 80A. This scheme will be wound down from 2026.

- SDE++  
With the SDE++ subsidy scheme, the government guarantees a minimum price for the supply of electricity to the grid for renewable energy.    
Most larger PV installations, both on roofs and on land, use this scheme,  
thanks to which the Netherlands is now in the global top 3 in terms of generation capacity per capita.  
Who is this scheme aimed at?

  - Grid connection of at least 3 x 80A

  - Central government organisations are excluded

- ‘Postcoderoos’ [a reduced rate scheme]/ SCE scheme 
The ‘Subsidieregeling Coöperatieve Energieopwekking’ [Cooperative energy generation subsidy scheme] enables neighbours to share in a PV project on a large roof.

- EIA/MIA/VAMIL 
These schemes encourage companies to become more sustainable through tax incentives, for instance through accelerated amortisation of investments made in measures to improve sustainability.

5.2 Financing

For most Sun-on-Roof projects, the owner or renter of the building also becomes the owner of the PV system. This raises the question of how to finance the project; fully self-finance through own resources or partly through external financial backers. External financial backing requires a financial model for the PV project, setting out revenue and expenditure, balances and cash flows over the project period.

There are two categories of financing, each with varying risks and returns:

- Through a loan - low risk and low return

Depending on the size of the project and the financial backer, 70 to 90% may be taken out as a loan, often at a low interest rate (2 to 5%). That means that you yourself will have to come up with only 10 to 30% of the project costs up front. Project revenue will first be allocated to the loan provider.

Typical conditions:

  - Minimum amount: EUR 1 million

Financial backers often require a minimum size due to the fact that there is a lot of work involved in a PV project loan. All the financial and technical details need to be reviewed, and contracts need to be assessed. This is not an automated task and continues to be labour-intensive. It is for this reason that financial backers apply a minimum loan size for a project (or for a number of combined projects from the same owner).

  - Additional requirements

The involvement of external financial backers will often mean that they set additional requirements in order to minimise risk. For instance, some banks will finance only PV modules from BNEF ‘tier 1’ suppliers; ‘tier 1’ status provides an indication of financial status only but says nothing about the quality or sustainability [of the installation].

- As a shareholder - risk-bearing capital

If a bank provides a loan, that often covers 70 to 90% of the project costs.  
The remaining 10 to 30% is deemed to be risk-bearing capital. This will be the first to be drawn on in the event of any problems or if the revenue falls short of expectations.

Project developers/EPCs will often put up part of the required equity; this means that they also bear the primary risk in the event of disappointing results. In this way, they lend extra credibility to the fact that the project has been properly completed.

In addition to the project developers, there are also various financial backers willing to help, for example, through crowdfunding or certain investment funds.

Significant risks involved with PV projects: Fire

Connectors are often a cause of fire in a PV installation. For instance, if the male and female connector in a DC cable are both of the MC4 type but made by different manufacturers. Or if a connector is wrongly fitted to the cable. Sometimes, the roof covering catches fire and there can be fire or smoke damage to the building and contents. Owing to the direct current in the DC cables (between the solar panels and the inverter), once an electric arc has occurred, it does not quickly right itself.

An electric arc can cause the connectors to reach extremely high temperatures and melt through the roof covering, after which the arc can cause flammable insulation materials (such as EPS) to ignite.  
Roof fires of this type are difficult to extinguish, and the whole building may be lost.

Solutions to this issue include:

- Electric arc detector with auto-shutdown (listed in the Template with requirements)

- Fire-resistant foils (such as Solardec) and coatings (such as Allshields)

- Fire-resistant casing of connectors (such as ArcBox).

Other measures are also important to minimise the risk of fire: the correct connectors; the correct installation of connectors; the sizing of cables; cable management; maintenance and monitoring, etc.

Significant risks involved with PV projects: Fire

Connectors are often a cause of fire in a PV installation. For instance, if the male and female connector in a DC cable are both of the MC4 type but made by different manufacturers. Or if a connector is wrongly fitted to the cable. Sometimes, the roof covering catches fire and there can be fire or smoke damage to the building and contents. Owing to the direct current in the DC cables (between the solar panels and the inverter), once an electric arc has occurred, it does not quickly right itself.

An electric arc can cause the connectors to reach extremely high temperatures and melt through the roof covering, after which the arc can cause flammable insulation materials (such as EPS) to ignite.  
Roof fires of this type are difficult to extinguish, and the whole building may be lost.

Solutions to this issue include:

- Electric arc detector with auto-shutdown (listed in the Template with requirements)

- Fire-resistant foils (such as Solardec) and coatings (such as Allshields)

- Fire-resistant casing of connectors (such as ArcBox).

Other measures are also important to minimise the risk of fire: the correct connectors; the correct installation of connectors; the sizing of cables; cable management; maintenance and monitoring, etc.

Overview of potential financial backers 
Triodos and ASN Bank, the large commercial banks, state-owned banks such as the BNG, and many other specialised funds and backers: please refer to Annex 5 for a list of financial backers2.

5.3 Insurance

Depending on the situation, various insurances may be appropriate. If you are paying for the project out of your own resources, you can weigh up the matter for yourself. If banks or other financial backers are involved in the project, they almost always ask for an ‘Operational All Risk’ (OAR) insurance and for the contracting party to have adequate business liability insurance (Bedrijfsaansprakelijkheidsverzekering - AVB).

Please find below a short description of four relevant types of insurance.

For Sun-on-Roof: Fire insurance

A number of building fires have been caused by PV installations over recent years. Premiums for buildings and contents insurance often increase as a result of the increased fire risk after a PV installation has been placed on the roof. The insurer may sometimes set additional requirements (e.g. an electric arc detector). The requirements must be included in the call for tenders or the contract description.

Tip. It is important to enquire about the costs of new or adapted insurance policies at an early stage. In some cases, premiums can be so high that they make the business case for the PV project unprofitable. This has proved to be the downfall of various 
PV projects.

Operational All Risk Insurance (OAR)

This insurance is taken out by the client itself. It protects against:

- Damage to the solar panel installation 
The OAR insurance covers damage to the PV installation as a result of external contingencies such as: fire, storm, lightning strike, theft or vandalism.

- Loss of production 
In the event of damage to the PV installation, it may be some time before it can be repaired or replaced, which can lead to loss of income. OAR insurance also covers loss of income as a result of damage.

Business Liability Insurance (AVB)

PV project requirements usually state that the contracting party must have adequate Business Liability Insurance to ensure a financial settlement in the event that it is found liable for any damage incurred during the works.

Some examples of coverage:

- Damage to property Damage to the client’s property (cars, building, etc.) caused by an accident during the works.

- Personal injury If anybody suffers a physical injury as a result of the contractor’s actions. This covers medical costs and any compensation for damages.

- Legal fees Covers, among other things, lawyers’ fees and legal costs if the company is involved in legal proceedings.

Coverage and conditions of an AVB vary from one insurance company to another and according to the type of company.

CAR (Construction All Risk) insurance

Installers/EPCs must have taken out and paid for CAR insurance with sufficient coverage (for example: EUR 1 million/at least of equal value to the contract value). As the client, you can also choose to take out CAR insurance yourself. It provides the same coverage, but you are the one ‘in control’. The insurance covers different risks to the ones covered by the AVB.

Annex 9 provides a short summary of what CAR insurance covers.

Step 6 Sustainability aspects

Point 6.1 will look briefly at the sustainability aspects of solar panels, while point 6.2 will succinctly examine the environmental aspects of solar farms and floating PV installations.

This document will not discuss installation materials and inverters. Installation materials are mostly made of aluminium or steel, which can both be easily recycled. Aluminium is often already made from recycled aluminium. As of yet, there is not much information on the differences in working life and robustness. Sustainable aspects of inverters and substructures will be looked at in a future version of this document.

6.1 Sustainability aspects of solar panels

Please find below a summary of the main sustainability aspects. These topics are dealt with extensively in the document ‘Sustainability aspects and market scan of more sustainable solar panels’, which also looks at the more sustainable options for sale, indicating the additional costs.

Tip. You should consider which sustainability aspects are the most important to your organisation at the preliminary stage. The above-mentioned document will help you estimate the additional costs of certain requirements, and also the impact on the number of suppliers and the business case.

| Issue | Explanation | In the Template with requirements? |
| --- | --- | --- |
| Carbon footprint of PV panels | Differs by a factor of 4 between the global top 20 of PV manufacturers: around 300 - 1200 kg CO2/kWp. In the Netherlands, for installations taking place in 2024, the CO2 payback time for mainstream solar panels is 8 to 20 years (depending on assumptions). It is 2 to 4 years for low carbon panels. Low-CfP panels are 5-20% more expensive. | Standard requirement: 550 kg CO2 per kWp according to the ‘Simplified Carbon Assessment’. Bonus points: for lower CfP: |
| Avoidable harmful materials | The back of many mainstream solar panels is entirely covered with a layer of PFAS, which poses a risk of soil pollution. Also, the solder often contains lead and there is antimony in the glass. PFAS-free solar panels are widely available. There are also a small number of solar panels that contain neither lead nor antimony. | Standard requirement: PFAS-free. Bonus points: Lead-free solder, antimony-free glass. |
| Working life | The technical working life of many solar panels, including those from ‘tier 1’ manufacturers, is probably 10 to 15 years. However, a working life of at least 30 years is also a good possibility when using high-quality materials and a robust design. These solar panels are 10 to 15% more expensive. | Bonus points: 30 years product guarantee, substantiated by tests. |
| Working conditions in the supply chain. | Forced labour involved in the manufacturing of solar cells has been documented in Xinjiang. There are various initiatives aiming to identify whether a manufacturer or their suppliers use forced labour (SER [Social and Economic Council of the Netherlands] agreement on international responsible business conduct regarding human rights; SolarPower Europe’s ‘Solar Stewardship Initiative’). | Requirements and objective criteria still being developed. |
| During the installation of the panels | The installation of solar panels in the Netherlands sometimes involves the exploitation of migrant workers. | Requirement: Supplier Code of Conduct. |
| Circularity | Various ideas and concepts are developed as ‘Design for Recycling’, including a commitment to use a certain percentage of recycled materials. | Requirements and objective criteria still being developed. |
| End-of-life | Replacement by other panels only in the event of a defect. The (compulsory) disposal contribution must be paid to the OPEN Foundation [Organisation for Producer Responsibility for E-waste Netherlands (OPEN)]. | Requirement: disposal contribution is paid. |

6.2 Environmental aspects involved in Sun-on-Land and 
Sun-on-Water

Sun-on-Land

Solar panels in PV installations on land with an East-West orientation are sometimes set so close together that barely any light or water can still reach the ground; this causes the soil life beneath the panels to disappear. A little more space for light and rain makes a huge difference. For further details see:

https://zoninlandschap.nl/u/files/ZonneparkenBeterOntwerpTNOV2.pdf

TNO has developed a soil test, which looks at whether or not sufficient soil life is possible, depending on the location, orientation and distance between the rows. Glass-glass panels provide some help too if the sunlight can also shine through the edges of the panel to the ground. The Template now also states that the Ground Coverage Ratio for smaller projects must be less than 70% and there must be gaps of at least 2 cm between the panels (for rainwater). Larger projects must comply with the TNO’s soil test.

Biodiversity may be promoted through certain herbs, plants or grasses, through a mowing policy or by installing an insect hotel.

Please note: the Sun-on-Land consortium is working on an eco-label for solar farms (EcoCertifified); this will set soon set out a number of guidelines.

Agrivoltaics (or Agrophotovoltaics)

Experience is also being developed in combining agriculture and PV generation (‘agrivoltaics’). Various solutions are used: from rows of vertically oriented solar panels to canopies of solar panels above fruit trees. Agrivoltaics is still at a relatively early stage.

Sun-on-Water

Within the ‘Sun-on-Water’ consortium, organisations such as Deltares and the Association of Regional Water Authorities [Unie van Waterschappen] are also examining the environmental aspects of floating PV installations. These studies are still in the early stages, and it is not yet clear whether or not any requirements in environmental terms need to be set. For further details see:  www.zonopwater.nl

Step 7 Execution and delivery

7.1 Timelines

With your organisation, decide when the work for the PV project could start; are there any other works that need to be taken into account?

In addition, discuss with a consultant what would be a realistic delivery date . This must take into account the time required for the call for tenders and the award of the contract and also the construction of the installation.

7.2 Inspections and final inspection

Scope 12 inspection

Upon delivery of all projects, be they large or small, on roofs, land or water, it is important to have an independent party carry out a safety inspection in accordance with protocol SCIOS Scope 12 (norm IEC62446).

This ‘Scope 12’ inspection checks the safety of the installation and reports any shortcomings relating to, among other things, electrical safety, mechanical safety against wind and snow, and lightning protection. It is stated as a requirement in the Template that the contracting party will subsequently correct any shortcomings identified (‘non-conformities’).

We would recommend that you request the Scope 12 inspection offers in due time. It could be difficult to find an inspector shortly before delivery and the rates may be higher.

Tip. As the client, you should always make the arrangements for the Scope 12 inspection yourself. Annex 6 provides a list of organisations that can carry out a Scope 12 inspection.

Large-scale projects: Sample tests on solar panels and factory audits

Large-scale projects (larger than 1MW) are also sometimes subject to sample tests and 
factory audits.

You should consider whether to include this in the call for tenders, whereby the contracting party would be responsible for organising it, or you can keep it out of the call for tenders and organise it yourself.

Sample tests Solar panels are sometimes supplied with a lower power than the one stated in the accompanying documentation. Sometimes, visible or invisible damage has occurred at the factory or during transport. This can end up costing a lot of money for large projects.

In large projects, a (very small) number of solar panels are tested after they arrive in the Netherlands and before they are released for installation. These sample tests check the quality of the solar panels delivered.

The tests examine such things as:

- does the stated Watt peak power match - using a flash test

- are there too many microcracks, increasing the likelihood of rapid degradation - using EL testing

- carrying out a visual inspection of the module - checking the assembly and finish

- performing an inspection of the module materials used - checking the specification.

A factory audit is often also performed for very large projects (larger than 20 MWp). This entails independent checking that the quality of the batch of solar panels ordered during the manufacturing process at the factory.

Samples tests and factory audits (often in China) are expensive. For a 10MW project, that can mean EUR 4 000 to 6 000 for the sample tests and EUR 5 000 to 8 000 for the factory audit.

Annex 7 provides a list of organisations that can carry out sample tests or factory audits2.

For smaller projects, the extra costs are generally not worthwhile, given the risk.

In addition, it is possible and customary to include a fixed yield guarantee for the first 2 to 4 years in the contract or call for tenders.

Step 8 Maintenance, Monitoring and End-of-Life

The operational phase starts when the PV project is delivered and producing electricity. Choices regarding this phase are made at the preliminary stage so that the requirements concerned are included or not in the schedule of requirements.

It is often the case that the installer/EPC that completed the PV installation is asked to provide 2 to 4 years of maintenance and monitoring. This provides an incentive for the contractor to deliver a good-quality installation with a high performance ratio.

Maintenance and monitoring can also be commissioned separately. It is also sometimes carried out by the in-house technical department.

Annex 8 provides a list2 of organisations that are involved in maintenance and monitoring.

Maintenance and repairs

This includes, among other things:

- Checking the inverter and cleaning it, if necessary

- Checking the cables and cable ducts

- Checking the construction

- Replacing any defective solar panels, if necessary

Cleaning

Solar panels are rarely cleaned in the Netherlands - the rain rinses them clean. Barring exceptional cases (e.g. lots of birds in the vicinity), the cost of cleaning is not justified by the extra yield.

Monitoring

The operational phase involves detecting and resolving any problems quickly. Homeowners often use their smartphone app to check that the inverter or the PV installation is working properly. For smaller projects, the technical department or the usual installation company will do this. For large projects, it can prove cost-effective to hire a specialised company to do this.

Monitoring comprises the remote reading of, among other things,

- the inverter and electricity meters,

- and comparing the yield from nearby systems, several times a year,

- for larger projects, using a drone with an infra-red camera to inspect the solar panels

Disposal contribution and replacement of solar panels

The Template with requirements states that the client pays the compulsory disposal contribution for the solar panels to the OPEN Foundation. Furthermore, solar panels should remain in place as long as possible in order to slow down climate change. After all, producing the panels emits a lot of CO2 and this can mean the CO2 payback time of solar panels 
can be years.

This is why it is recommended to remove solar panels only when they yield less than around 80% of their initial yield. High-quality solar panels will generate more than 80% of their initial yield for at least 25 to 30 years.

Abbreviations and acronyms

| EPC | Engineering, Procurement, Construction | MPP | Maximum Power Point |
| --- | --- | --- | --- |
| O&M | Operations & Maintenance | MPPT | Maximum Power Point Tracker |
| Voc | Open circuit Voltage | PPA | Power Purchase Agreement |
| LCOE | Levelised Cost of Electricity | kW | kiloWatt |
| HV | High Voltage | kWh | kiloWatt hour |
| LV | Low Voltage | PV | PhotoVoltaic |
| AC | Alternating Current | PR | Performance Ratio |
| DC | Direct Current | EN | European Norm |
| Isc | Short Circuit Current | c-Si | Crystalline Silicon |
| °C | Degrees Centigrade | POA | Plane of Array |
| CE | Conformity to European standards | RTB | Ready To Build |
| GHI | Global Horizontal Irradiance | SPV | Special Purpose Vehicle - a legal entity used in financing constructions |
| CAR | Construction All Risk | EL | Electro-Luminescence test - Reveals microcracks and broken cells |
| PAC | Provisional Acceptance Criteria | FAC | Final Acceptance Criteria |
| kVA | kiloVoltAmpere; Power; similar to kW | MW | Megawatt |
| PID | Potential Induced Degradation | PM | Project Manager |
| PVGIS | Photovoltaic Geographical Information System | Q&A | Question & Answer |
| RfP | Request for Proposal | STC | Standard Test Conditions (25 C, 1 000 W/m2 irradiance) |
| UV | Ultraviolet | TMY | Typical Meteorological Year |
| Impp | Current at Maximum Power Point | Vmpp | Voltage at Maximum Power Point |
| IR | Infra Red - e.g. drones use IR cameras for quality inspections | PL | Photoluminescence |
| ESG | Environmental Social Governance | AQL | Acceptable Quality Limit |
| RfG | Requirements for Generation | RTB | Ready to Build |
| BAFO | Best and Final Offer |  |  |

Annex 1 - Technical Consultants2

Please note: The list below is not exhaustive. We have not carried out any research into the experience, quality or rates of the consultants listed below.

| Company | Place of establishment | Contact | Email |
| --- | --- | --- | --- |
| Encon | Nijmegen, NL |  |  |
| Straight Forward | Urmond, NL |  |  |
| Pulsar Power | Herentals, BE |  |  |
| 3E | Brussels, BE |  |  |
| DNV | Arnhem, NL |  |  |
| Sunzest Solar | Rotterdam, NL |  |  |
| Solar Chills | Haarlem, NL |  |  |
| DevCon Ecosystems | Zaandam, NL |  |  |

Annex 2 - Building physics consultants, structural engineers specialising in roof load2

Please note: The list below is not exhaustive. We have not carried out any research into the experience, quality or rates of the consultants listed below.

| Company | Place of establishment | Contact | Email |
| --- | --- | --- | --- |
| Dakbestek Adviesburo | Vught, NL |  |  |
| Van Doorn Dakspecialist | Rilland, NL |  |  |
| ABT | Delft, NL |  |  |
| DGMR | Arnhem, NL |  |  |
| Buro Bouwfysica | Cappelle aan de Ijssel, NL |  |  |
| Tritium | Breda, NL |  |  |

Annex 3 – Installation companies, 
EPCs and project developers 
for PV companies2

Please note: The list below is not exhaustive. We have not carried out any research into the experience, quality or rates of the consultants listed below.

| Type of company | Company | Website | Email |
| --- | --- | --- | --- |
| Large electrical and technical installation companies | Unica | www.unica.nl |  |
|  | Hoppenbrouwers | www.hoppenbrouwerstechniek.nl |  |
|  | Batenburg | www.batenburg.nl |  |
|  | Spie | www.spie-nl.com |  |
|  | Croon Elektrotechniek | www.croonwolterendros.nl |  |
| Large solar installation companies/ EPCs | Zonnegilde | www.zonnegilde.nl |  |
|  | SolarNRG |  |  |
|  | Zonnestroom Nederland | www.zonnestroomnederland.nl |  |
|  | Eigen Energie | www.eigenenergie.net |  |
|  | Groenleven | www.groenleven.nl |  |
|  | Ecorus | www.ecorus.nl |  |
|  | SENS | www.sens-energy.com |  |
|  | Solar Partners | www.solarpartners.nl |  |
|  | UniSun | www.unisun-energy.eu |  |
|  | Goldbeck | www.goldbeck.nl |  |
|  | KiesZon | www.kieszon.nl |  |
|  | OranjeDak | www.oranjedak.nl |  |
|  | SunProjects | www.sunprojects.nl |  |
|  | Izen | www.izen.eu |  |
|  | Pfzal Solar | www.pfzalsolar.com |  |
|  | Engie | www.engie.com |  |
|  | Belectric | www.belectric.com |  |
|  | ProfiNRG | www.profinrg.nl |  |
| Project developers | Groenleven | www.groenleven.nl |  |
|  | Klimaatfonds | www.klimaatfonds.nl |  |
|  | TPSolar | www.tpsolar.nl |  |
|  | GreenIpp | www.greenipp.com |  |
|  | Encavis | www.encavis.com |  |
|  | Tomorrow Energy | www.tomorrowenergy.nl |  |
|  | HVC Groep | www.hvcgroep.nl |  |
|  | Nara Solar | www.narasolar.com |  |
|  | Statskraft | www.statkraft.com/ |  |
|  | Pure Energie | www.pure-energie.nl |  |
|  | LC Energy |  |  |
|  | Enovos | www.enovosgreenpower.eu |  |
|  | Lightsource BP | www.lightsourcebp.com/nl/ |  |
|  | Chint Solar | www.chintsolar.nl |  |
|  | SunVest | www.sunvest.nl |  |
|  | SunProjects | www.sun-projects.nl |  |
|  | Vattenfall | www.vattenfall.com |  |
|  | Ecorus | www.ecorus.com |  |
|  | Eneco | www.eneco.com |  |
|  | Powerfield | www.powerfield.nl |  |
|  | Novar | www.novar.nl |  |
|  | Groendus | www.groendus.nl |  |
|  | IB Vogt | www.ibvogt.com |  |

Annex 4 - Consultants and providers specialised in energy management systems, batteries, and demand management2

Please note: The list below is not exhaustive. We have not carried out any research into the experience, quality or rates of the consultants listed below.

| Company | Place of establishment | Contact | Email |
| --- | --- | --- | --- |
| Peta Watts BV | Rotterdam |  |  |
| Lyv energy | Blaricum |  |  |
| European Solar | Heerenveen |  |  |
| Scholt Energy | www.scholt.nl |  |  |
| Odura | www.odura.nl |  |  |
| StoredEnergy | Schiedam |  |  |
| MorePV | Schoorl |  |  |
| Alfen | www.alfen.com |  |  |
| Fudura | Zwolle |  |  |
| Encon | Nijmegen, NL |  |  |

Annex 5 - Loan capital

and equity capital backers2

Please note: The list below is not exhaustive. We have not carried out any research into the experience, quality or rates of the consultants listed below.

| Financing type | Company | Website | Email |
| --- | --- | --- | --- |
| Loan capital | Commerzbank | www.commerzbank.com |  |
|  | KfW Bank | www.kfw.de |  |
|  | Rabobank | www.rabobank.nl |  |
|  | ING | www.ing.com |  |
|  | Triodos | www.triodos.nl |  |
|  | ASN Bank | www.asnbank.nl |  |
|  | BNG Bank | www.bngbank.nl |  |
| Crowdfunding | Zonnepanelen Delen | www.zonnepanelendelen.nl |  |
|  | Duurzaaminvesteren | www.duurzaaminvesteren.nl |  |

Annex 6 - Scope 12 inspections2

Please note: The list below is not exhaustive. We have not carried out any research into the experience, quality or rates of the consultants listed below.

| Company | Place of establishment | Website | Email |
| --- | --- | --- | --- |
| Omega Energie Techniek | Vianen, NL | www.omega-energietechniek.nl |  |
| RJ Inspecties | Best. NL | www.rjinspecties.nl |  |
| Entheq Inspecties |  | www.entheq.nl |  |
| Wassenaar Inspecties | Wassenaar, NL | www.wassenaarinspecties.nl |  |
| GreenHero Inspecties en Opledingen | Dronten, NL | www.greenhero.nl |  |
| Stroomwijs | Apeldoorn, NL | www.stroomwijs.nl |  |
| Install Keur | Woerden, NL | www.install-keur.nl |  |
| TUV Nord | Son, NL | www.tuvnord.nl |  |
| EKCN | Beverwijk, NL | www.ekcn.nl |  |

Annex 7 - Factory audits 
and sample testing2

Please note: The list below is not exhaustive. We have not carried out any research into the experience, quality or rates of the consultants listed below.

| Company | Place of establishment | Website | Email |
| --- | --- | --- | --- |
| Sinovoltaics | Hong Kong, CN | www.sinovoltaics.com |  |
| Odin Spire/Sunchine | Rotterdam, NL | www.eternalsunspire.com |  |
| CEA | Shanghai, CN | www.cea3.com |  |
| Solar Tester | Schinnen, NL | www.solartester.nl |  |
| STS | Shanghai, CN | www.sts-certified.com |  |
| PI Berlin | Berlin, DE | www.pi-berlin.com |  |

Annex 8 - Monitoring, maintenance 
and repairs2

Please note: The list below is not exhaustive. We have not carried out any research into the experience, quality or rates of the consultants listed below.

| Company | Place of establishment | Website | Email |
| --- | --- | --- | --- |
| Zonnepark Services Nederland | Utrecht, NL | www.zonnepark-services.nl |  |
| Solora | Hilversum, NL | www.solora.nl |  |
| Everday | Rosmalen, NL | www.everday.eu |  |
| Stern Energy | Schoorl. NL | n.a. |  |

Annex 9 - Overview of CAR insurance coverage

Section I: The works

The works are those agreed in the building contract. The amount insured for the building work is the costs of repairs for restoration to the pre-damage state.

Risks covered by a CAR policy: flooding, wind, earthquakes, water damage and mould, construction defects and negligence.

Normal wear and tear and deliberate negligence are not covered.

Advanced disruption of operations (optional)

This covers any financial loss of the insured party resulting from the interruption of the contracted work, which causes delays in the scheduled start of commercial operations.

Section II: Liability

The liability clause covers the liability of the insured party and other parties - for examples the contractors - vis-à-vis third parties for events connected to the performance of the work, such as:

- injury to persons

- loss of, damage to or destruction of material property.

In addition, there is also the liability of the insured parties vis-à-vis each other. If the contracting party causes damage to the client (both insured under the policy), the contracting party can submit a claim under the policy since its liability to the client is covered.

Section III: Existing property of the client

Damage to the existing property of the client resulting from the works insured. The damage must therefore be a direct consequence of the works carried out.

Section IV: Contractor’s materials

Damage to the contractor’s equipment caused by external events, such as storm, fire and theft. Such equipment includes scaffolding, frameworks, cabins, sheds, tools, etc., which need to be on site as part of the works. The following are excluded: sailing and floating equipment, draglines, bulldozers, cranes and other mechanically propelled means of transport.

Heading V: Property of the management and staff

Damage to personal property belonging to the management and staff of the insured party, which occurred on site and was caused by external events, such as storms and theft. The following are excluded:

- cash and valuable documents, etc.,

- mechanically propelled vehicles.

Section VI Transport

This paragraph covers damage to or theft of building materials during transport.
The important factor for coverage in this section is that:

- transport must be charged to and at the risk of the insured party;

- cover must extend from loading to unloading on site

https://wetten.overheid.nl/BWBR0032203/2022-03-02/0

This report is version 1.0, and additional names may be added at a later stage.

See also: UvW 2021-XX Praktische handreiking ZOW sjabloon UvW versie jan 2022.pdf (stowa.nl)

For instance: Tibber, ANWB Energy, NextEnergy, Eneco, EnergyZero, Zonneplan, Frank Energie, Innova

For instance: Edmij, Energypool, Scholt, Sympower

If you are renting a roof or land out to a PV project developer, then that party will be in charge of financing.